January 30, 2023

Fire Marshal Pre-Application Conference comments

Knife River Concrete Batch Plant

PAC-2023-00027

Bryan Mattson, Project Planner

This application was reviewed by Jason Knoble in the Fire Marshal's Office.  Jason can be reached at (564) 397-3318 or e-mail at Jason.knoble@clark.wa.gov.    Where there are difficulties in meeting these conditions or if additional information is required, contact Jason in the Fire Marshal's office immediately.

Building construction occurring subsequent to this application shall be in accordance with the provisions of the county's building and fire codes.  Additional specific requirements may be made at the time of building construction as a result of the permit review and approval process.

Fire flow in the amount of 1000 gallons per minute supplied for 120 minutes duration is required for this application.  Prior to obtaining building permits, submit proof from the water purveyor indicating that the required fire flow is available at the site.  Water mains supplying fire flow and fire hydrants shall be installed, approved and operational prior to the commencement of combustible building construction.  Fire flow is based on a non-sprinklered 2,000 square foot building of type VB construction.

Fire hydrants are required for this application.  The indicated number and spacing of the fire hydrants is adequate.

Fire apparatus access is required for this application.  The roadways and maneuvering areas as indicated in the application adequately provide required fire apparatus access.  Provide fire apparatus access roads with an unobstructed width of not less than 20 feet, an unobstructed vertical clearance of not less than 13.5 feet, with an all-weather driving surface and capable of supporting the imposed loads of fire apparatus.  Access roads shall extend to within 150 feet of all portions of the facility and all portions of the exterior walls of the first story of the building.

Approved fire apparatus turnarounds are required for this project.  The indicated provisions for turning around fire apparatus are adequate.

No gate may be installed across a required fire department access road or driveway without first obtaining a permit from the fire marshal’s office.  Inspection and testing of the gate will be required.  Split gates with a divided entry and exit side will need 15 feet on either side for a total gate width of 30 feet.

Parking is prohibited on access roads that are less than twenty-four (24) feet wide. Roads that are less than twenty-four (24) feet wide shall be posted "NO PARKING-FIRE LANE".

New and existing buildings must have approved radio coverage for emergency responders as outlined by Section 510 of the fire code and may require the installation of an Emergency Responder Radio Coverage System (ERRCS).  Proof of adequate radio coverage will be required.  A separate permit is required to install or modify an ERRCS and related equipment.  For more information, contact CRESA Radio Department at (360) 992-9222.

Jason Knoble

Senior Deputy Fire Marshal

These comments are based on the information provided with the pre-application materials.  Any revision to the proposal may change the Fire Marshal comments.